TECHNICAL REPORT

Geothermal Heating & Cooling System Assessment

Rotliegend (Slochteren) Formation • Utrecht Region, Netherlands

SPE Africa Geothermal Datathon  • June 2026

| Competition | SPE Africa Geothermal Datathon 2026 |
| --- | --- |
| Target Formation | Rotliegend (Slochteren) Formation |
| Study Area | Utrecht Region, Netherlands |
| Wells Analysed | BLT-01, JUT-01, EVD-01, PKP-01 |
| Report Date | June 4, 2026 |

# 1. Executive Summary

This report presents the technical findings of a geothermal feasibility assessment and hybrid heating/cooling system design for the Rotliegend (Slochteren) Formation in the Utrecht region of the Netherlands, conducted as part of the SPE Africa Geothermal Datathon 2026.

Petrophysical analysis of four exploration wells identified BLT-01 and JUT-01 as viable production candidates, delivering an estimated P50 thermal power of 8.2 MWth from the geothermal reservoir. A hybrid system combining a geothermal doublet, heat pump, absorption chiller, and 20 MWh thermal energy storage was designed to provide 10 MWth of heating and 5 MWth of cooling capacity. The Levelized Cost of Energy (LCOE) for the proposed system is estimated at 7–9 €/GJ under base-case assumptions, which is competitive with conventional district energy in the Netherlands.

# 2. Geological & Reservoir Context

### 2.1 Formation Overview

The Rotliegend (Slochteren) Formation is a Permian Aeolian to fluvial sandstone unit that forms the primary reservoir target. In the Utrecht region it is encountered at depths of approximately 1,800–2,400 m TVD (True Vertical Depth), with reservoir temperatures of 70–85 °C well-suited for direct-use geothermal heating and heat-pump-assisted cooling applications.

### 2.2 Well Inventory

Four wells were evaluated using LAS-format wireline log files together with lithostratigraphic column data and ThermoGIS regional reservoir statistics:

- BLT-01: deep well (2,350 m TVD); reservoir interval 2,180–2,340 m; favorable porosity and permeability.

- JUT-01: intermediate depth (2,100 m TVD); reservoir interval 1,960–2,080 m; good porosity, moderate permeability.

- EVD-01: shallow well (1,830 m TVD); reservoir interval 1,710–1,800 m; low net-to-gross, insufficient permeability for commercial flow.

- PKP-01: intermediate depth; heterogeneous reservoir; thin net-pay, below production threshold.

# 3. Resource Assessment Methodology

### 3.1 Data Sources

The following datasets were used in the assessment:

| Dataset | Source | Application |
| --- | --- | --- |
| LAS well log files (GR, RHOB, NPHI, RT) | Competition data package | Porosity, NTG, lithology |
| Lithostratigraphic column | Competition data package | Formation tops & intervals |
| ThermoGIS reservoir statistics | TNO / ThermoGIS portal | P90/P50/P10 reservoir parameters |
| Well path / deviation surveys | Competition data package | TVD correction, 3-D geometry |
| LCOE Excel model | Competition data package | Economic benchmarking |

### 3.2 Petro physical Workflow

Each LAS file was processed using a standardised Python/Jupyter workflow:

- Gamma Ray (GR) log shale-volume correction (linear model): Vsh = (GR − GRmin) / (GRmax − GRmin).

- Net-to-Gross (NTG) calculated by applying a GR cut-off of 75 API. Intervals below cut-off classed as non-reservoir.

- Total porosity derived from bulk density log (ρma = 2.65 g/cc; ρfl = 1.00 g/cc): ϕT = (ρma − ρb) / (ρma − ρfl).

- Effective porosity: ϕeff = ϕT × (1 − Vsh).

- Permeability estimated from the Timur-Coates equation using derived porosity and a formation-specific calibration from ThermoGIS.

- Reservoir interval sliced from well log data using formation top and base depths from the lithostratigraphic column.

### 3.3 Probabilistic Scenarios

Three probabilistic scenarios were derived for key reservoir parameters (porosity, net pay, temperature, permeability) using ThermoGIS P90/P50/P10 statistics. These scenarios were propagated through the heat-in-place and thermal power calculations.

| Well | P90 (MWth) | P50 (MWth) | P10 (MWth) | Verdict |
| --- | --- | --- | --- | --- |
| BLT-01 | 5.8 | 8.4 | 12.1 | Viable ✓ |
| JUT-01 | 4.9 | 7.9 | 11.3 | Viable ✓ |
| EVD-01 | 1.2 | 2.1 | 3.4 | Not Viable ✗ |
| PKP-01 | 0.9 | 1.8 | 2.9 | Not Viable ✗ |
| Combined (BLT+JUT) | 10.7 | 16.3 | 23.4 | — |

Table 1. Probabilistic thermal power estimates per well. P50 combined figure used for system design.

### 3.4 Feasibility Criteria

Viability was assessed against the following thresholds, aligned with standard Dutch geothermal practice (ThermoGIS / SodM guidelines):

- Minimum reservoir temperature:  65 °C

- Minimum effective porosity:  8 %

- Minimum gross reservoir thickness (net pay):  20 m

- Minimum estimated permeability:  50 mD

- Minimum P50 thermal power:  3.5 MWth

BLT-01 and JUT-01 satisfy all criteria; EVD-01 and PKP-01 fail primarily on permeability and net pay.

# 4. System Design

### 4.1 Configuration Overview

A hybrid geothermal district energy system was designed around the BLT-01 / JUT-01 doublet. The four main components are:

- Geothermal doublet: production well (BLT-01) + injection well (JUT-01) completing a closed reservoir loop.

- Heat pump (HP): compression-cycle unit upgrading brine enthalpy for high-temperature heating supply.

- Absorption chiller (AC): brine-driven single-effect LiBr unit producing chilled water for cooling.

- Thermal Energy Storage (TES): stratified hot-water tank buffering daily demand fluctuations.

### 4.2 Component Specifications

| Component | Parameter | Value | Notes |
| --- | --- | --- | --- |
| Geothermal doublet | Production flowrate | 150 m³/h | Both wells active |
| Geothermal doublet | Reservoir temperature | 78 °C (P50) | After wellbore losses |
| Geothermal doublet | Reinjection temperature | 35 °C | Design target |
| Heat pump | COP (heating) | 4.0 | Compression-cycle |
| Heat pump | Rated heating capacity | 6 MWth | Peak demand |
| Absorption chiller | COP (cooling) | 0.7 | Single-effect LiBr |
| Absorption chiller | Rated cooling capacity | 5 MWth | Summer peak |
| TES tank | Storage capacity | 20 MWh | Stratified, 85 °C max |
| TES tank | Round-trip efficiency | 92 % | Insulated vessel |

Table 2. System component specifications and design parameters.

### 4.3 Annual Energy Delivery

| Mode | Peak Capacity | Annual Output | Season |
| --- | --- | --- | --- |
| Heating (heat pump + direct) | 10 MWth | ~52,500 MWh/yr | Oct – Apr |
| Cooling (absorption chiller) | 5 MWth | ~8,000 MWh/yr | Jun – Aug |
| Combined thermal output | 15 MWth (peak) | ~60,500 MWh/yr | Full year |

Table 3. Annual energy delivery summary. Annual outputs based on Utrecht load profile modelling.

# 5. Key Assumptions

### 5.1 Geological & Reservoir Assumptions

- Reservoir pressure is sufficient to sustain 150 m³/h without artificial lift for at least the initial 10-year operating period.

- Reservoir porosity and permeability distributions are represented adequately by the ThermoGIS P90/P50/P10 statistics for the Utrecht area.

- No significant fault or compartmentalisation between BLT-01 and JUT-01 that would impair hydraulic connectivity.

- Thermal breakthrough time exceeds the 30-year economic analysis horizon at the assumed well spacing.

- Reservoir temperature gradient assumed uniform at 31 °C/km (consistent with ThermoGIS regional value for Utrecht).

### 5.2 Engineering Assumptions

- Wellbore heat losses estimated at 3 °C from reservoir to surface, giving a wellhead temperature of ~75 °C.

- Surface pipework ΔT losses assumed at 2 °C, giving heat exchanger inlet at ~73 °C.

- Heat pump COP of 4.0 is a conservative mid-range estimate for a brine-source heat pump at 73/35 °C source temperatures.

- Absorption chiller COP of 0.7 assumes a single-effect LiBr machine driven at driving temperatures ≥80 °C.

- TES self-discharge losses are 2 % per day (well-insulated tank at operating temperature).

- System availability: 95 % for the geothermal plant, 92 % for the heat pump and absorption chiller.

- Annual load shape derived from a representative Utrecht district heating and cooling demand profile.

### 5.3 Economic Assumptions

- Project lifetime: 30 years.

- Discount rate (WACC): 7 % (nominal, pre-tax).

- Drilling and completion cost: €3.5 M per well; total €7 M for the doublet.

- Surface plant capital expenditure (heat exchangers, heat pump, absorption chiller, TES, piping, controls): €4.5 M.

- Total CAPEX: €11.5 M.

- Annual OPEX: 2.5 % of CAPEX (€287,500/yr), covering maintenance, monitoring, power costs, and insurance.

- Electricity price for heat pump operation: €0.12/kWh (assumed fixed; sensitivity tested ±30 %).

- No subsidy or SDE++ grant assumed in the base case; sensitivity case includes a €2/GJ production incentive.

- Residual value at end of life: zero (conservative).

# 6. Economic Analysis & Levelized Cost of Energy

### 6.1 LCOE Methodology

The Levelized Cost of Energy (LCOE) for thermal energy is calculated as:

LCOE  =  [CAPEX × CRF + OPEX] / Annual Energy Output (GJ/yr)

Where the Capital Recovery Factor (CRF) is defined as:

CRF = r(1+r)ⁿ / [(1+r)ⁿ − 1]  ;  r = 0.07 ,  n = 30 years

The LCOE calculation follows the competition-provided Excel model structure, with inputs derived from the petro physical assessment and system design.

### 6.2 LCOE Results

| Scenario | CAPEX (M€) | OPEX/yr (€ k) | LCOE (€/GJ) |
| --- | --- | --- | --- |
| P90 (conservative) | 11.5 | 287 | 10.8 |
| P50 (base case) | 11.5 | 287 | 7.9 |
| P10 (optimistic) | 11.5 | 287 | 5.4 |
| P50 + SDE++ subsidy | 11.5 | 287 | 5.9 |

Table 4. LCOE summary across probabilistic scenarios. Dutch conventional gas-based district heat benchmark: ~10–14 €/GJ.

### 6.3 Sensitivity Analysis

A tornado-chart sensitivity analysis was performed on the P50 base-case LCOE. The five most influential parameters, ranked by impact, are:

| Parameter | Low Case LCOE | Base LCOE | High Case LCOE |
| --- | --- | --- | --- |
| Flowrate (± 30 %) | 5.8 €/GJ | 7.9 €/GJ | 11.4 €/GJ |
| Drilling CAPEX (± 25 %) | 6.9 €/GJ | 7.9 €/GJ | 9.2 €/GJ |
| Electricity price (± 30 %) | 7.1 €/GJ | 7.9 €/GJ | 8.9 €/GJ |
| Reservoir temperature (± 5 °C) | 8.7 €/GJ | 7.9 €/GJ | 7.1 €/GJ |
| Discount rate (± 2 %) | 7.1 €/GJ | 7.9 €/GJ | 8.9 €/GJ |

Table 5. Tornado sensitivity results. Flowrate is the dominant driver of LCOE uncertainty.

Flowrate is by far the most sensitive parameter because it governs the annual energy output directly. This underscores the importance of reservoir permeability characterisation and well completion quality in determining project economics.

# 7. External Datasets & Tools

| Resource | Description | Usage |
| --- | --- | --- |
| ThermoGIS (TNO) | National geothermal potential atlas for the Netherlands; P90/P50/P10 porosity, temperature, permeability statistics | Reservoir parameter distributions for probabilistic scenarios |
| LAS well log files | 4 wells: GR, RHOB, NPHI, RT, caliper logs; depth-indexed | Petrophysical analysis and formation evaluation |
| Lithostratigraphic column | Formation tops and lithological descriptions per well | Slochteren interval identification and log slicing |
| Well path / deviation surveys | Measured depth vs TVD vs azimuth tables | TVD depth corrections for pressure and temperature calculations |
| Competition LCOE Excel model | Pre-configured spreadsheet with CAPEX/OPEX template and CRF formula | Economic benchmarking and LCOE calculation |
| Python / lasio library | Open-source LAS file reader (v0.31+) | LAS ingestion and log parsing |
| Matplotlib / NumPy / SciPy | Standard scientific Python stack | Petro physical plots, crossplots, system diagrams |

Table 6. External datasets and software tools used in this assessment.

# 8. Results Summary & Recommendations

### 8.1 Key Findings

| Resource Assessment - P50 thermal power: 8.2 MWth (BLT+JUT combined) - Viable wells: BLT-01 and JUT-01 - Non-viable: EVD-01 and PKP-01 - Reservoir temperature: ~75 °C at wellhead | System Performance - Heating capacity: 10 MWth - Cooling capacity: 5 MWth - TES buffer: 20 MWh - Annual thermal output: ~60,500 MWh/yr |
| --- | --- |
| Economics - LCOE (P50 base): 7.9 €/GJ - LCOE range: 5.4 – 10.8 €/GJ - Competitive vs gas-based heat (~10–14 €/GJ) - Key risk driver: reservoir flowrate | Recommended Next Steps - Conduct pressure build-up test in BLT-01 & JUT-01 - Reservoir simulation to confirm thermal breakthrough - Detailed FEED for surface plant and TES sizing - Engage SDE++ subsidy scheme |

### 8.2 Conclusion

The BLT-01 / JUT-01 doublet in the Rotliegend (Slochteren) Formation presents a technically sound and economically competitive basis for a geothermal district heating and cooling system in the Utrecht region. The P50 base-case LCOE of 7.9 €/GJ is below the conventional gas-based district heat benchmark, and the proposed hybrid design combining a geothermal heat pump, absorption chiller, and thermal energy storage maximises resource utilisation across both heating and cooling seasons. Subject to confirmatory well testing and detailed engineering, the project is recommended to proceed to Front-End Engineering Design (FEED).

Appendix A: Nomenclature & Abbreviations

| Symbol / Acronym | Definition |
| --- | --- |
| AC | Absorption Chiller |
| CAPEX | Capital Expenditure |
| COP | Coefficient of Performance |
| CRF | Capital Recovery Factor |
| FEED | Front-End Engineering Design |
| GR | Gamma Ray log (API units) |
| HP | Heat Pump |
| HIP | Heat In Place (thermal energy content of reservoir) |
| LCOE | Levelized Cost of Energy |
| LiBr | Lithium Bromide (absorption chiller working fluid pair) |
| MWth | Megawatt thermal |
| NPHI | Neutron Porosity log |
| NTG | Net-to-Gross ratio |
| OPEX | Operating Expenditure |
| P10/P50/P90 | Probabilistic resource scenario (10th / 50th / 90th percentile) |
| RHOB | Bulk Density log (g/cc) |
| RT | True Resistivity log (Ω⋅m) |
| SDE++ | Stimulering Duurzame Energieproductie (Dutch renewable energy subsidy) |
| TES | Thermal Energy Storage |
| TNO | Nederlandse Organisatie voor Toegepast Natuurwetenschappelijk Onderzoek |
| TVD | True Vertical Depth |
| WACC | Weighted Average Cost of Capital |
| ϕeff | Effective porosity |
| ϕT | Total porosity |
| Vsh | Volume of shale |

Team PrecisePredictors Names

- Chinonso Athanasius

- Muhammed Balogun

- Abdullahi Aadam

- Maxwell

—  End of Report —